| M S RAMAIAH INSTITUTE OF TECHNOLOGY USN | 1 | M | S |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

(AUTONOMOUS INSTITUTE, AFFILIATED TO VTU)

BANGALORE – 560 054

MAKEUP EXAMINATIONS – JULY 2016

| Course & Branch | : | B.E. – Electrical & Electronics Engg. | Semester | : | VI |
| --- | --- | --- | --- | --- | --- |
| Subject | : | Generation , Economics & Reliability Aspects of Power Systems | Max. Marks | : | 100 |
| Subject Code | : | EEPE42 | Duration | : | 3 Hrs |

Instructions to the Candidates:

- Answer one full question from each unit.

|  |  | UNIT -I |  |  |
| --- | --- | --- | --- | --- |
| 1. | a) | Enumerate on the pros and cons of nuclear power plant. | C01 | (06) |
|  | b) | Explain fuel supply system and lubricating system of a diesel power plant with suitable diagrams. | C01 | (06) |
|  | c) | Write brief notes on (i) Air preheater and (ii) Superheater | C01 | (08) |
| 2. | a) | Draw and explain the fuel handling system of a modern thermal power plant. | C01 | (06) |
|  | b) | Compare and contrast the steam, hydro and nuclear power plants with respect to initial cost, running cost, maintenance cost and transmission and distribution cost. | C01 | (08) |
|  | c) | Explain the functions of the following with respect to nuclear power plant - Control rod (ii) reflector and (iii) moderator | C01 | (06) |
|  |  | UNIT – II |  |  |
| 3. | a) | A generating station has a maximum demand of 25MW, a load factor of 60%, a plant capacity factor of 50% and a plant use factor of 72%. Find (i) daily energy produced (ii) reserve capacity and (iii) maximum energy that could be produced daily if the plant were fully loaded. | C01 | (06) |
|  | b) | An industrial consumer has the following loads during a year 20MVA,0.8pf for 2000hrs 10MVA, 0.8pf for 1000hrs 2MVA, 0.8pf for 500hrs ;Both are step down transformers of 20MVA each Particulars; Transformer 1; Transformer 2. Full load Efficiency; 0.985; 0.99. Core loss in KW; 120; 90. Second transformer is costlier by Rs.1,00,000 and the interest and depreciation is 15%. Cost of energy is Rs.0.40/kWh.Select which alternative is cheaper? | C01 | (10) |
|  | c) | Discuss the advantages of interconnected system. | C01 | (04) |
| 4. | a) | The energy cost of a 100MW steam station working at 40% load factor comes out to be 12 p/kWh of energy generated. What will be the cost of energy generated if the load factor is improved to 60%? The fuel cost of the power station due to increased generation increase the annual generation cost by 5%. | C01 | (08) |
|  | b) | A power station has to meet the following demand: Group A : 200kW between 8a.m and 6 p.m Group B: 100kW between 6 am and 10 am Group C: 50kW between 6 am and 10 am Group D:100kW between 10 am and 6 pm and then between 6 pm and 6 am. Plot the daily load curve and determine (i) diversity factor (ii) units generated per day and (iii) load factor. | C01 | (08) |
|  | c) | What is tariff? Explain block rate and flat rate tariff. | C01 | (04) |
|  |  | UNIT-III |  |  |
| 5. | a) | How are the hierarchical levels in are power system are classified. | CO2 | (05) |
|  | b) | List the factors effecting the reliability of the power systems. | CO2 | (05) |
|  | c) | A small generating plant is designed to satisfy a constant 10 MW load Three alternatives are being considered i)1x 10 MW unit ii)2x10 MW unit iii)3x 5MW unit Prepare the capacity outrage probability table for each of three alternatives. | CO2 | (10) |
| 6. | a) | What is the significance of IEEE real test systems . | CO2 | (05) |
|  | b) | Probabilistic technique is better than analytic technique . Justify. | CO2 | (05) |
|  | c) | For the following LDC curve calculate the EIR with system having three identical units of having capacity 100 MW with FOR 0.02 ? | CO2 | (10) |
|  |  | UNIT- IV |  |  |
| 7. | a) | Why are load curtailment techniques necessary ? Explain its philosophy. | CO2 | (06) |
|  | b) | State and explain the main deffernce between the ENEL and U of S method in composite system adequacy evaluation. | CO2 | (10) |
|  | c) | Define outage and discuss its classfications. | CO2 | (04) |
| 8. | a) | Write short notes on (i) contingency enumeration approach (ii) Station originated outages. | C02 | (10) |
|  | b) | What is Monte Carlo Simulation? Mention its advantages and disadvantages. State any four indices that can be computed in MCS. | C02 | (10) |
|  |  | UNIT- V |  |  |
| 9. | a) | What is IEAR? How is it calculated? Explain. | C02 | (10) |
|  | b) | Explain the assessment of reliability worth involving the interruption cost for residential users. | C02 | (10) |
| 10. | a) | Find SAIFI,SAIDI,CAIDIASAI for the following set of customer data Line; failure rate; Repair rate; No.of customers; Avg.load demand. A; 0.20; 6.00; 200; 1000. B; 0.10; 5.00; 150; 700. C; 0.15; 8.0; 100; 400. | C03 | (10) |
|  | b) | What is Interruption Energy Assessment Rate? What are the factors that contribute to its variation. | C03 | (10) |

**********************