RAMAIAH

Institute of Technology

| USN | 1 | M | S |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

(Autonomous Institute, Affiliated to VTU)

(Approved by AICTE, New Delhi & Govt. of Karnataka)                       Accredited by NBA & NAAC with ‘A’ Grade

SEMESTER END EXAMINATIONS –  JANUARY 2019

| Course & Branch | : | B.E: Electrical and Electronics Engineering | Semester | : | VII |
| --- | --- | --- | --- | --- | --- |
| Subject | : | High Voltage Engineering | Max. Marks | : | 100 |
| Subject Code | : | EE73 | Duration | : | 3 Hrs |

Instructions to the Candidates:

- Answer one full question from each unit.

|  |  | UNIT- I |  |  |
| --- | --- | --- | --- | --- |
| 1. | a) | With necessary equations discuss the streamer theory for breakdown in gaseous dielectrics. | CO1 | (08) |
|  | b) | Discuss time lag in the context of discharge in gaseous dielectric. | CO1 | (06) |
|  | c) | An air bubble of 0.25 mm thickness is embedded in a solid insulation of 2cm thickness having relative dielectric constant of 3. The voltage applied across the solid dielectric is 50kV (rms), 50Hz. Calculate the voltage at which internal discharge occurs. | CO1 | (06) |
| 2. | a) | What is work function of a metal? Why a positive ion requires the energy level twice the work function of a metal to dislodge an electron from it? | CO1 | (04) |
|  | b) | Define Townsend’s first and second ionization coefficients and derive an expression for the current growth in a gas discharge due to secondary ionization. | CO1 | (10) |
|  | c) | State, prove and explain the Paschens law. | CO1 | (06) |
|  |  | UNIT- II |  |  |
| 3. | a) | Explain the breakdown in solid dielectrics due to treeing and tracking. | CO1 | (06) |
|  | b) | Draw a three stage Cockroft Walton voltage multiplier circuit and explain the working of it. | CO1 | (08) |
|  | c) | Discuss the bubble formation in a liquid dielectric and explain how it leads to the breakdown. | CO1 | (06) |
| 4. | a) | A ten stage Cockroft-Walton circuit has all capacitors of 0.08µF. The secondary voltage of the supply transformer is 125kV at a frequency of 100Hz. If the load current is 5mA, determine (i)voltage regulation (ii)the ripple (iii) the optimum number of stages for maximum output voltage (iv) the maximum output voltage. | CO1 | (08) |
|  | b) | With necessary equations and waveforms explain the breakdown in a solid dielectric due to internal discharges. | CO1 | (08) |
|  | c) | Explain intrinsic breakdown of a solid dielectric. | CO1 | (04) |
|  |  | UNIT- III |  |  |
| 5. | a) | Explain the working principle of resonant transformer and how is it advantageous over the cascade-connected transformers? | CO2 | (10) |
|  | b) | For the single stage impulse generator shown in the Fig.5(b), obtain an expression for the output. Fig.5(b) | CO3 | (10) |
| 6. | a) | A 5-stage impulse generator has capacitors each rated at 0.05µF, 20kV. The capacitance of the test specimen is 1000pF. Determine the wave front, wave tail resistances and efficiency to produce a 1.2/50µs impulse wave using approximate formulae. | CO3 | (06) |
|  | b) | How are rectangular current pulses generated for testing purposes? How is their time duration controlled? | CO3 | (06) |
|  | c) | An impulse current generator is rated for 60kW-s. The parameters of the circuit are C=53µF, L=1.47µH and the dynamic resistance=0.0156 ohm. Determine the peak value of the current and the time-to-front and the time-to-tail of the current waveform. | CO3 | (08) |
|  |  | UNIT- IV |  |  |
| 7. | a) | With neat sketch explain High ohmic series resistance with microammeter method for the measurement of high voltage DC and also mention its merits and demerits. | CO4 | (08) |
|  | b) | Explain the Chubb Fortscue method for measurement of high voltage AC peak. | CO4 | (08) |
|  | c) | List the factors affecting the measurement of high voltages using standard spheres. | CO4 | (04) |
| 8. | a) | With neat sketch explain the generating voltmeter construction and working for the measurement of high voltages. | CO4 | (10) |
|  | b) | Explain resistance potential divider for measurement of very low impulse voltages and fast rising pulses. | CO4 | (10) |
|  |  | UNIT- V |  |  |
| 9. | a) | Explain the high voltage Schering bridge for the tanδ and capacitance measurement of insulation. | CO5 | (10) |
|  | b) | What are partial discharge? Discuss the method of balanced detection for locating partial discharges in electrical equipment. | CO5 | (10) |
| 10. | a) | Explain different types of tests conducted on insulators. | CO5 | (08) |
|  | b) | Explain the method of impulse testing of high voltage transformers. What is the procedure adopted for locating the failure? | CO5 | (12) |

****************