RAMAIAH

Institute of Technology

| USN | 1 | M | S |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

(Autonomous Institute, Affiliated to VTU)

(Approved by AICTE, New Delhi & Govt. of Karnataka)                       Accredited by NBA & NAAC with ‘A’ Grade

MAKEUP EXAMINATIONS –  APRIL 2021

| Program | : | B.E. : Electrical and Electronics Engineering | Semester | : | VII |
| --- | --- | --- | --- | --- | --- |
| Course Name | : | Switchgear and Protection | Max. Marks | : | 100 |
| Course Code | : | EE71 | Duration | : | 3 Hrs |

Instructions to the Candidates:

- Answer one full question from each unit.

|  |  | UNIT- I |  |  |
| --- | --- | --- | --- | --- |
| 1. | a) | Explain the fuse law. Name the material with which fuse is made. | CO1 | (05) |
|  | b) | Define “Fuse”. With neat sketch explain the construction and working of a high voltage liquid type fuse. | CO1 | (10) |
|  | c) | Explain the difference between isolating switch and load break switch. | CO1 | (05) |
| 2. | a) | Discuss energy balance theory of arc interruption in a circuit breaker. | CO1 | (05) |
|  | b) | In a 110 kV system, the reactance and capacitance up to the location of the circuit breaker is 4Ω and 0.010µF respectively. A resistance of 300 Ω is connected across the contacts of the circuit breaker. Determine the following: - Natural frequency of the oscillation. - Damped frequency of the oscillation. - Circuit value of the resistance which will give no transient oscillation. - The value of resistance which will give damped frequency of oscillation one fourth of the natural frequency. | CO1 | (08) |
|  | c) | Derive an expression for restriking voltage and RRRV in terms of System voltage inductance voltage and capacitance. | CO1 | (07) |
|  |  | UNIT – II |  |  |
| 3. | a) | What are the advantages and disadvantages of minimum oil circuit breaker? | CO2 | (05) |
|  | b) | With neat sketch, explain construction and working of vacuum circuit breaker. | CO2 | (10) |
|  | c) | Explain any one type of Puffer type SF6 circuit breaker. | CO2 | (05) |
| 4. | a) | Explain the need for Protective systems. | CO2 | (05) |
|  | b) | Explain with a neat diagram – “Zones of Protection”. | CO2 | (10) |
|  | c) | Explain primary and Back-up protection. | CO2 | (05) |
|  |  | UNIT – III |  |  |
| 5. | a) | What is distance protection? In what way a distance relay is superior to over-current protection for protection of transmission lines. | CO3 | (06) |
|  | b) | An IDMT type overcurrent relay is used to protect a feeder through 500/1A CT. The relay has a plug setting of 125% and TMS = 0.3. Find the time of operation of the said relay if a fault current of 5000 A flows through the feeder. Make use of the following characteristics: (100% current = 1A) PSM; 2; 3; 5; 8; 10; 15. Time for Unity TMS; 10; 6; 4.5; 3.2; 3; 2.5. | CO3 | (06) |
|  | c) | With the help of a block diagram, explain the operating principle of a static directional overcurrent relay. | CO3 | (08) |
| 6. | a) | With the help of time – current characteristics curve, compare various types of overcurrent relays. Mention applications and general time current equations for each one of them. | CO3 | (10) |
|  | b) | With relevant circuit and phasor diagrams, discuss how static reactance relay can be realized using i) amplitude comparator ii) phase comparator. Explain its characteristics on the R-X diagram. | CO3 | (10) |
|  |  | UNIT – IV |  |  |
| 7. | a) | Mention the faults that are likely to occur in a three phase induction motor? Distinguish between short circuit protection, overload protection and earth fault protection of motor. | CO4 | (06) |
|  | b) | A 5000 kVA, 6600 V, star connected alternator has a synchronous reactance of 2 ohms per phase and resistance of 0.5 ohms per phase. It is protected by a Merz – Price balanced current system which operates when out of balance current exceeds 30% of load current. Determine what proportion of alternator winding is unprotected if the star point is earthed through a resistance of 6.5 ohms. | CO4 | (08) |
|  | c) | With neat sketches, discuss differential schemes for bus zone protection. | CO4 | (06) |
| 8. | a) | Why is it necessary to suppress the field immediately after disconnection of faulty alternator from the system? Explain. | CO4 | (04) |
|  | b) | A three phase, 33000/6600V transformer is connected in star/delta and the protecting current transformer on the low voltage side have a ratio of 300/5. What will be the ratio of the current transformer on the high voltage side? | CO4 | (06) |
|  | c) | What is carrier aided distance protection? What are its different types? With the help of trip circuit and solid state logic, explain permissive over-reach transfer tripping scheme of protection. | CO4 | (10) |
|  |  | UNIT – V |  |  |
| 9. | a) | With the help of a relevant diagram, explain how adoptive relaying can be used to reduce plug setting of the differential relay used for protection of a transformer. | CO5 | (10) |
|  | b) | With the help of a flow chart, explain how a microprocessor based impedance relay can be realized. | CO5 | (10) |
| 10. | a) | With a relevant sketch, explain the concept of adaptive control of dependability and security of protection systems based on WAMS. | CO5 | (10) |
|  | b) | With the help of a neat sketch explain how hierarchy is established between PMUs and PDCs to manage WAMS. | CO5 | (10) |

****************