RAMAIAH

Institute of Technology

| USN | 1 | M | S |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

(Autonomous Institute, Affiliated to VTU)

(Approved by AICTE, New Delhi & Govt. of Karnataka)                       Accredited by NBA & NAAC with ‘A’ Grade

SUPPLEMENTARY SEMESTER EXAMINATIONS – SEPTEMBER 2021

| Program | : | B.E. : Electrical and Electronics Engineering | Semester | : | VII |
| --- | --- | --- | --- | --- | --- |
| Course Name | : | Switchgear and Protection | Max. Marks | : | 100 |
| Course Code | : | EE71 | Duration | : | 3 Hrs |

Instructions to the Candidates:

- Answer any five full questions.

| 1. | a) | Briefly explain different methods through which resistance of the arc can be increased in a circuit breaker. | CO1 | (05) |
| --- | --- | --- | --- | --- |
|  | b) | In a 132 kV system, the circuit phase to ground capacitance is 0.01F, the inductance is 6H. Calculate the voltage appearing across the pole of a circuit breaker if the magnetizing current of 10A is interrupted (instantaneous value). Calculate the value of resistance to be used across contact space to eliminate the restriking voltage transients. | CO1 | (05) |
|  | c) | What are the factors to be taken into consideration when selecting a fuse for: i) Transformer protection ii) Motor protection iii) Capacitor protection iv) Heater v) lightning load. | CO1 | (10) |
| 2. | a) | In a short circuit test on a three pole, 132 kV circuit breaker, the following observations are made: PF of fault is 0.4, the recovery voltage is 0.9 times full line value, the breaking current is symmetrical, the frequency of oscillation of restriking voltage is 16 kHz. Assume that the neutral is grounded and the fault does not involve ground. Determine the average rate of rise of restriking voltage. | CO1 | (08) |
|  | b) | What are the different types of fuses? Discuss with a neat sketch the construction and working of HRC fuse. | CO1 | (08) |
|  | c) | Explain the phenomenon of current chopping in a circuit breaker. | CO1 | (04) |
| 3. | a) | Bring out the classification of the circuit breakers based on the arc quenching medium. Also mention their operating voltage range and breaking capacity. | CO2 | (05) |
|  | b) | Describe with a neat sketch the principle of operation of minimum oil circuit breaker. Bring out the advantages and disadvantages of minimum oil circuit breaker with respect to bulk oil circuit breaker. | CO2 | (10) |
|  | c) | Explain the basic difference between a CT used for instrumentation and a CT used for protection. | CO2 | (05) |
| 4. | a) | A three phase circuit breaker is rated at 2000 MVA, 33 kV. Find its making current. | CO2 | (04) |
|  | b) | Compare and contrast air circuit breaker and oil circuit breaker. | CO2 | (06) |
|  | c) | With a neat sketch explain the construction and working of vacuum circuit breaker. Bring out its advantages and disadvantages. | CO2 | (10) |
| 5. | a) | What are the different types of distance relays? Compare their merits and demerits. Discuss their field of applications. | CO3 | (07) |
|  | b) | With the help of waveforms, explain the concept of coincidence circuit type phase comparator. | CO3 | (05) |
|  | c) | With the help of a block diagram, explain static inverse time over current relay. | CO3 | (08) |
| 6. | a) | With relevant circuit and phasor diagrams, discuss how static MHO relay can be realized using i) amplitude comparator ii) phase comparator. Explain its characteristics on the R-X diagram. | CO3 | (10) |
|  | b) | With a neat circuit diagram and characteristics curve, explain percentage differential relay. | CO3 | (10) |
| 7. | a) | Explain the term “single phasing”. In what form such protection is provided in case of a large 3 phase induction motor? If the motor is not fully loaded, is it necessary to provide protection against single phasing? Explain why? | CO4 | (07) |
|  | b) | A 55 MVA, 132/66 kV, Delta/star, three phase power transformer is protected by percentage differential relays. If the current transformers located on delta and star sides of the power transformer are 300/5A and 1200/5A respectively, determine i) the output current at full load ii) the relay current at full load iii) the minimum relay current setting to permit 25% overload. | CO4 | (08) |
|  | c) | List the common types of generator faults. Explain protection against bearing overheating. | CO4 | (05) |
| 8. | a) | What type of protection scheme is employed for the protection of a large power transformer against short circuits? With a neat sketch discuss its working principle. | CO4 | (07) |
|  | b) | Find the portion of winding protected against earth fault on a 11 kV, 50 MVA star connected alternator having a reactance of 1.5 ohm per phase and negligible resistance. The generator neutral is grounded with 10 ohm resistor. Merz – Price protection scheme is used which operates when the out of balance current exceeds 5% of the full load current. | CO4 | (08) |
|  | c) | What are the abnormal operating conditions experienced by an AC Motor? Explain stalling condition in an AC motor. | CO4 | (05) |
| 9. | a) | Draw the Block diagram of microprocessor based over current relay and explain. | CO5 | (10) |
|  | b) | With the help of relevant diagram, explain how adoptive relaying can be used to reduce plug setting of the differential relay used for protection of a transformer. | CO5 | (10) |
| 10. | a) | With the neat diagram explain how hierarchy is established between PMUs and PDCs to manage WAMS. | CO5 | (10) |
|  | b) | With a Flow chart, explain how microprocessor based impedance relay can be realized. | CO5 | (10) |

****************